ANNEXURE 1

Here is a relevant section , from a very long narrative document of a  USEPA decision, to permit disposal of treated sewage water into a well, even where it is suspected that it may contaminate Underground Source of Drinking Water ( USDW) in Florida.

USEPA modified an earlier rule of "No Fluid Movement from the injection well to USDW, and revised the Rule by specifying BOD , SS and Chlorine levels ( and no other parameters) in the treated water prior to disposal :

REFERENCE

# Underground Injection Control Program--Revision to the Federal Underground Injection Control Requirements for Class I Municipal Disposal Wells in Florida

[Federal Register: November 22, 2005 (Volume 70, Number 224)]
[Rules and Regulations]
[Page 70513-70532]
From the Federal Register Online via GPO Access [wais.access.gpo.gov]
[DOCID:fr22no05-12]

-----------------------------------------------------------------------

ENVIRONMENTAL PROTECTION AGENCY
40 CFR Part 146
[FRL-7999-7]

Underground Injection Control Program--Revision to the Federal 
Underground Injection Control Requirements for Class I Municipal 
Disposal Wells in Florida

AGENCY: Environmental Protection Agency.
ACTION: Final rule.

THE FINAL RULE

"""1. Selected Approach

The following sections outline EPA's rationale for the specific

requirements in today's rule, including requiring pretreatment,

secondary treatment, and high-level disinfection, as well as the

rationale for not requiring the removal of other contaminants and why

the new treatment will be phased in over time.

a. Rationale for Requiring Pretreatment of Wastewater. Today's rule

includes requirements for owners and operators of facilities that wish

to be covered by the alternative endangerment standard to comply with

existing pretreatment requirements for those facilities. EPA found that

almost all (14 of the 16) facilities that have caused or may cause

fluid movement into a USDW already have pretreatment programs in place,

and the remaining two facilities have conducted surveys indicating that

they are not handling waste streams from significant industrial users.

EPA believes that existing pretreatment programs at the affected

facilities are adequate and necessary to ensure that a variety of

contaminants that might appear in wastewater do not endanger USDWs.

EPA agrees with commenters who suggested that requiring industrial

users to pretreat their wastewater would reduce the chance of

contaminating USDWs and reduce the costs to municipal treatment works.

EPA also agrees with several commenters who advocated extending

pretreatment requirements to facilities with flows of less than 5 MGD.

EPA disagrees with commenters who opposed the pretreatment

requirements, and who cited concerns about the ineffectiveness of

pretreatment programs to prevent fluid movement or protect public

health. EPA believes that it is important for significant industrial

users to pretreat their wastewater to remove those contaminants that

would not be consistently removed by a municipal wastewater treatment

facility before they are injected.

Therefore, today's rule requires that owners and operators develop

and implement a pretreatment program that is no less stringent than the

State's requirements in Florida Rule 62-625, unless they have no

significant industrial users as defined in that chapter, if they wish

to avail themselves of the alternative endangerment standard. The State

developed these pretreatment requirements to ensure that contaminants

are prevented from endangering the public. EPA is adopting pretreatment

provisions consistent with those requirements under the authority of

the SDWA to prevent contaminants from endangering USDWs.

b. Rationale for Requiring Secondary Treatment of Wastewater.

Florida currently requires Class I municipal wastewater facilities to

apply secondary treatment prior to injection, and this requirement will

stay in place regardless of the addition of the high-level disinfection

requirement. Applying secondary treatment, which requires BOD reduction

to 25 ppm and TSS reduction to 30 ppm, is necessary for high-level

disinfection to work. Without significant reduction in suspended solids

that is first achieved by secondary treatment and is further addressed

by filtration, the standards for compliance with the high-level

disinfection standard of 5 ppm of total suspended solids in this rule

could not be achieved."""

Dr. Ananth S. Kodavasal – Director					September 18, 2009

Ecotech Engineering Consultancy Pvt. Ltd.

39, Dodsworth Enclave

Whitefield, Bangalore 560 066

Tel/ Fax : 28454760

Mobile   : 98450-62033

Email    : kodavaas@bgl.vsnl.net.in

ecotech.bangalore@gmail.com